## Slide 1: Session 4: Advanced HMI
Tommy Morris
Professor, Electrical and Computer Engineering
Director, Center for Cybersecurity Research and Education
University of Alabama in Huntsville

## Slide 2: Connection Errors
Make sure the data sources are enabled.
Make sure your PLC is reachable over the network.
  Is it running?
  Is the correct program running?
  Is the network up?

## Slide 3: Connection Errors
For the Arduino setup the PLC is running on the host PC.
The SCADABr is in a VM with a host-only network configuration.
From SCADABr the PLC is reached at 192.168.56.1
  This address is configurable in Virtual Box
    The host IP address can be found (and set) under Preferences -> Network -> Host Only Networks
    Select the appropriate adapter

## Slide 4: CONNECTION ERRORS
Under Data Sources: Use the Transport Type “TCP with Keep-alive”. This prevents the session from closing after a timeout.

## Slide 5: Connection ISSUES
Click here to enable all data sources
on
off

## Slide 6: Connection Issues
Click here to edit an individual input output point
Click here to enable all points
Click here to enable an individual input/output point

## Slide 7: Wrong Data on HMI
Check the
  Register range: is this the correct data type?
    %IX: Input status
    %QX: coil status
    %QW, MW, MD, ML: holding register
    %IW: input register
  Modbus data range: is this the correct data type?
    Input status and coil status can only be binary.
    The holding register and input register types have multiple valid lengths. Make sure this matches the ladder logic variable type and %QW, MW, MD, ML declaration.
  Offset is the address in the Modbus memory map for this variable.

## Slide 8: OpenPLC Addressing
I/O Memory Mapping
Address Translation
%QX & %IX
Modbus Address = whole part * 8 + decimal part
%IW & %QW
Modbus Address = whole part + decimal part

## Slide 9: OpenPLC Addressing
Regular Memory Map
Address translation - Modbus register addresses count in 16-bit word units.
%MW Modbus Address = 1024 + whole part
%MD Modbus Address = 2048 + 2*whole part
%ML Modbus Address = 4096 + 4*whole part

## Slide 10: OpenPLC I/O Addressing w/Arduino Uno
Type | Arduino Pin | OpenPLC Editor Address | SCADABr Address (aka. Modbus address)
Digital Inputs (Contact) | 2 | %IX100.0 | 800
 | 3 | %IX100.1 | 801
 | 4 | %IX100.2 | 802
 | 5 | %IX100.3 | 803
 | 6 | %IX100.4 | 804
Digital Outputs (Coil) | 7 | %QX100.0 | 800
 | 8 | %QX100.1 | 801
 | 12 | %QX100.2 | 802
 | 13 | %QX100.3 | 803
Type | Arduino Pin | OpenPLC Editor Address | SCADABr Address (aka. Modbus address)
Analog Inputs (input registers) | A0 | %IW100.0 | 100
 | A1 | %IW100.1 | 101
 | A2 | %IW100.2 | 102
 | A3 | %IW100.3 | 103
 | A4 | %IW100.4 | 104
Analog Outputs (holding registers) | 9 | %QW100.0 | 100
 | 10 | %QW100.1 | 101
 | 11 | %QW100.2 | 102

## Slide 11: nUMERIC INPUT from the HMI to the PLC - sIMPLE POINT COMPONENT
Analog Graphic -> Simple Point
  Displays the value of a register.
  Select the point to display.
Warning. Can’t read address over network.

## Slide 12: SCADABR Numeric Input
Define variable in ladder logic program
  16-bit word: %MW0 - %MW1023
  32-bit double word : %MD0 - %MD1023
  64-bit long word: : %ML0 - %ML1023
  In HMI use Component -> Simple point
  Check “settable” in Data Sources
  Check “Settable override” and “Display controls” in simple point configuration
Hover over the graphic to set the value
You cannot change the text size.

## Slide 13: SIMPLE POINT COMPONENT
  Config options:
  Point name override: display different text
  To enable writing from HMI to PLC:
    select “Settable override” and select “display controls”
  Display point name: select to show point name (with override if selected above)

## Slide 14: Binary Input FROM HMI
Method 1: Button (write)
  Use Component -> Button (write)
    Select point to display/control
    Set labels for on/off states
    Set height and width
  The button will have a different label for each state.

## Slide 15: BINARY INPUT FROM HMI
Method 2: Binary graphic
  Place a Component -> Binary graphic on the workspace
  Select the point
  Select “settable override” and “display controls”
  Choose an image set Note: these are named in Portuguese. Select each image to see an example of each.
  Set the 0 and 1 images.
This method takes input from the keyboard when the user hovers over the image. The image changes according to the setting (0 and 1 images correspond to 0 and 1 settings).

## Slide 16: Exercise
Develop Ladder Logic to turn on/off a LED if any of the following three conditions are true.
  (1) button press
  (2) number1 (16-bit INT) is greater than number2 (16-bit INT)
    These should be observable and settable in the HMI
    Hint use %MW0 and %MW1
  (3) binary input (override) from HMI is 1
    Hint use %QX101.0
Develop a corresponding HMI
  Display and edit number1 and number2
  Display the status of the LED using a binary graphic.
  Use a button(write) component to set the override state.

## Slide 17: Ladder Logic Solution - Variables

## Slide 18: Ladder Logic Solution

## Slide 19: Add a Blinking LED
Add a blinking LED that is on for 500ms then off for 500ms
  Use two TON function blocks to blink the LED.
Add a binary input to enable the LED from the HMI
Display a blinking LED in the HMI when the LED is blinking

## Slide 20: BLINKING LED - Variables

## Slide 21: BLINKING LED Ladder LOGIC
At time 0 timer2_out is 0. The negated contact starts TON0. timer1_out starts high while TON0 counts 500ms.
At time 500ms timer1_out goes low. This triggers TON1 to set timer2_out high.

## Slide 22: Arduino Shields
Use these expansion boards to build demos that you can reuse.
Solder components to the board.
  Resistors, LED, etc.
Less likely to be damaged when storing in a box
Easy to change between demos.
https://www.sparkfun.com/products/13820
There are also similar products called Pi Hats for Raspberry PI.